## Slide 1
NORTHSTAR COMPUTE
Shared compute for
university AI
Texas reference proposal | Customer discussion | October 2026
Notes: Based on the project Phase 1 design and the customer decision explorer. This is a reference proposal, not an approved construction project.

## Slide 2
NORTHSTAR COMPUTE
02
Decision requested
Advance Texas diligence.
Hold full capital approval.
The next gate is a written utility schedule and cost, member demand commitments, a site-specific resilience design, and priced vendor offers.
Notes: Source: internal Phase 1 design specification, sections 7.6 and 7.7; decision memo. The recommendation is conditional.

## Slide 3
NORTHSTAR COMPUTE
03
Texas leads the location assessment
Chart: 
| Texas | Québec | Helsinki
Weighted score | 3.6 | 3.05 | 3.05
3.60
Texas weighted score
Demand proximity carries the largest weight in the rubric.
Scores are planning judgments on a five-point scale.
Notes: Source: internal Phase 1 site selection, section 7.4. Texas 3.60, Québec 3.05, Helsinki 3.05. Demand proximity is 25 percent of the weighted rubric.

## Slide 4
NORTHSTAR COMPUTE
04
Reference design
20 MW
IT demand
25 MW
Total facility demand
219 GWh
Annual energy
PUE 1.25 is the planning assumption. Cooling uses a closed-loop, non-evaporative design.
Notes: Calculation: 20 MW IT x 1.25 PUE = 25 MW facility. 25 MW x 8,760 hours / 1,000 = 219 GWh per year. Source: internal Phase 1 design specification.

## Slide 5
NORTHSTAR COMPUTE
05
Power continuity
Fault isolation
Protection separates the failed component.
UPS transition
Critical load stays powered while alternate supply starts.
Backup operation
Generation sustains load, with shedding if capacity tightens.
A 48-hour grid outage at full facility load represents 1,200 MWh of delivered energy.
Notes: Calculation: 25 MW facility x 48 hours = 1,200 MWh. Backup fuel quantity, refuelling, permits and actual topology require site-specific engineering.

## Slide 6
NORTHSTAR COMPUTE
06
Investment structures
Build and own
More control over the facility and capacity. Highest initial capital exposure.
Lease capacity
Lower initial capital commitment. Vendor terms and long-run service cost matter most.
Phased hybrid
Stages ownership while leasing capacity. Limits early commitment but adds coordination.
The live explorer applies the same power price, utilization, PUE and grid-delay inputs to all three paths.
Notes: The site includes editable example inputs to demonstrate sensitivity. No vendor quote or financing commitment is represented in this slide.

## Slide 7
NORTHSTAR COMPUTE
07
Conditions for the next gate
01
Written utility energization schedule and connection cost
02
Applicable large-load and curtailment terms
03
Site-specific resilience and backup-power study
04
Closed-loop cooling through design and permitting
05
Member demand commitments and priced vendor offers
Notes: Source: internal Phase 1 section 7.6 and the decision memo. The fifth line combines member demand and vendor pricing, both needed before a capital decision.

## Slide 8
NORTHSTAR COMPUTE
08
Live decision explorer
Compare sites. Walk the design.
Change the assumptions.
global-datacenter-design-explorer-test.stephxu700296.chatgpt.site
Next decision: fund diligence and return with site-specific evidence.
Notes: Public test Site URL at the time of this presentation. Login is temporarily disabled for demo viewing; existing auth work is retained for the final access phase.